10 Step Checklist for Reducing Unwanted Fire Signals
1. Break-glass call points: / Relocate them to areas with less traffic if possible. / Consider protective covers to deter accidental breakage.	☐ / ☐
2. Testing and Maintenance: / Inform your Alarm Receiving Centre (ARC) before system testing to avoid triggering unnecessary responses. / Schedule regular preventative maintenance by a qualified engineer following BS 5839 standards.	☐ / ☐
3. Smoking: / Enforce a clear no-smoking/vaping policy and display prominent signage.	☐
4. Cooking Activities: / Maintain proper ventilation systems to remove smoke and grease particles. / Educate staff on proper cooking practices to minimize smoke generation. / Consider heat detectors in kitchens as an alternative to smoke detectors.	☐ / ☐ / ☐
5. Maintenance: / Clean detector heads regularly and maintain the system as per BS 5839 standards. / Maintain fire safety logbooks with detailed maintenance records.	☐ / ☐
6. Faulty Equipment: / Replace malfunctioning detectors and call points promptly. / Investigate and address the cause of system faults immediately.	☐ / ☐
7. Detector Placement: / Ensure detectors are the appropriate type for the area (e.g., heat detectors in kitchens). / Position detectors strategically following BS 5839 guidelines for full coverage.	☐ / ☐
8. Insect Activity: / Consider using pet flea collars or citronella oil around detectors as deterrents (during peak insect seasons).	☐
9. Aerosol Sprays and Steam: / Restrict the use of aerosols in areas with smoke detectors. / Explore alternative air fresheners and insect repellents. / Relocate detectors away from potential steam sources (kitchens, bathrooms).	☐ / ☐ / ☐
10. Dust Buildup: / Maintain good housekeeping practices to minimize dust accumulation.	☐